## Sheet1
DISCLAIMER:
These area statements are only indicative, not meant to be taken as a prescription.
I am not responsible for any errors or omissions in these statements.
They are presented here for your guidance only.
Architectural Area Statement
Proposed 300-Bed Hospital
Distribution of In-Patient Beds
Beds | Units | Beds / Unit | No. of Beds
Deluxe Rooms | 8 | 1 | 8
Private Rooms | 48 | 1 | 48
Semi-Private Rooms | 48 | 2 | 96
4-Bed Wards | 12 | 4 | 48
LDR's | 2 | 1 | 2
SICU | 2 | 12 | 24
MICU | 1 | 12 | 12
ICCU | 1 | 12 | 12
CT ICU | 1 | 12 | 12
Neuro ICU | 1 | 12 | 12
NICU | 1 | 8 | 8
PICU | 1 | 12 | 12
Daycare | 1 | 12 | 12
Total In-Patient Beds |  |  | 306
Intensive Care Beds are 35% of total bedstrength.
Modular ICU's + ICU Support @ 12 Bed Module
Area/Bed |  |  | 914.904
Total Built-Up Area of Hospital
Description |  |  | Area
Public Areas |  |  | 14112
Casualty Department |  |  | 5291
Out-Patient Department |  |  | 16146
Physotherapy & Rehabilitation |  |  | 1086
Radiology / Imaging & Diagnostics |  |  | 5000
Dialysis Unit |  |  | 2756
Radiation Therapy |  |  | 8424
Nuclear Medicine |  |  | 3458
Operation Theater Complex & Day Care Unit |  |  | 8424
Interventional Cardiology (Cath. Lab.) |  |  | 3679
Maternity Center + IVF |  |  | 6747
Nursery & NICU |  |  | 2379
Intensive Care Unit |  |  | 35243
In-Patient Wing |  |  | 71344
Central Sterilization & Processing Department |  |  | 2064
Clinical Laboratory & Blood Bank |  |  | 4992
Kitchen & Dining |  |  | 6072
Administration |  |  | 8040
Materials Management, Housekeeping, Laundry & Staff Lockers |  |  | 8487.5
Electrical, HVAC, Maintenance & Bio-Medical Engineering |  |  | 10224
Sub-Total |  |  | 223968.5
Add : Vertical Circulation, Fire Escapes, AHU's & BUA Factor @ 25% |  |  | 55992.125
Total |  |  | 279960.625
Public Areas
Description | Quantity | Area/Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Wheelchair / Stretcher Alcove | 2 | 50 | 100
Main Entrance Lobby | 1 | 7500 | 7500
Public Toilets | 2 | 300 | 600
Staff Toilets | 2 | 40 | 80
Reception & Front Office Staff Work Area | 1 | 250 | 250
Admitting / Discharge Cubicles | 5 | 50 | 250
Bank Extension Counter | 1 | 250 | 250
Billing Section | 1 | 300 | 300
PRO's Office/Social Workers Office | 1 | 120 | 120
Retail Pharmacy & Convenience Store | 1 | 750 | 750
Gift Shop cum Florist | 1 | 300 | 300
Telephone Booths | 6 | 20 | 120
Snack Bar | 1 | 400 | 400
EPABX/Server Room | 1 | 300 | 300
Prayer Room | 1 | 400 | 400
Housekeeping Closet | 2 | 20 | 40
Sub Total |  |  | 11760
(Add : Circulation @ 20%) |  |  | 2352
Total |  |  | 14112
Casualty Department
Description | Quantity | Area/Room | Total Area
|  | (sq. ft.) | (sq. ft.)
Triage | 1 | 400 | 400
Wheelchair / Stretcher Alcove | 2 | 50 | 100
Public Waiting | 1 | 500 | 500
Minor OT | 1 | 300 | 300
Change Cubicle | 1 | 30 | 30
Emergency Procedure Room cum Plaster Room | 2 | 200 | 400
Observation Beds | 12 | 100 | 1200
Scrub Stations | 2 | 25 | 50
Public Toilets | 2 | 120 | 240
Staff Toilets | 2 | 40 | 80
Support
Central Nurse Station | 1 | 150 | 150
Clean Utility | 1 | 100 | 100
Dirty Utility | 1 | 100 | 100
Mobile X-ray Alcove | 1 | 50 | 50
Staff Change | 2 | 75 | 150
Doctors Duty Room with Toilet | 1 | 180 | 180
Housekeeping Closet | 2 | 20 | 40
Sub-Total |  |  | 4070
Add : Circulation @ 30% |  |  | 1221
Total |  |  | 5291
Out-Patient Department
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Consultation Rooms/ Dedicated Doctor's Offices | 36 | 120 | 4320
Dental Clinic | 2 | 200 | 400
Opthalmic Clinic | 1 | 200 | 200
Laser Room | 1 | 120 | 120
A & B Scan, Perimetry | 1 | 200 | 200
ENT OPD | 1 | 150 | 150
Audiometry | 1 | 150 | 150
Executive Health Check-Up Lounge with Toilet | 1 | 750 | 750
Life Style Related Diseases-Exam & Consult | 1 | 1200 | 1200
Chemotherapy | 8 | 100 | 800
Chemotherapy Nurse Station | 1 | 100 | 100
Patient Toilet | 1 | 40 | 40
Minor Treatment Room | 2 | 200 | 400
Sample Collection / Injection with Toilet | 2 | 150 | 300
Sub-Waiting Areas | 6 | 120 | 720
Central Waiting Space | 1 | 1200 | 1200
Support
Nurse Station & Registration | 1 | 250 | 250
Clean Utility | 1 | 100 | 100
Dirty Utility | 1 | 100 | 100
Public Toilets | 2 | 300 | 600
Staff Toilets | 2 | 40 | 80
Wheelchair Alcove | 4 | 50 | 200
Housekeeping Closet | 2 | 20 | 40
Sub-Total |  |  | 12420
Add : Circulation @ 30% |  |  | 3726
Total |  |  | 16146
Physotherapy & Rehabilitation
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Reception/Waiting | 1 | 200 | 200
Change/Locker Rooms + Toilets | 2 | 350 | 700
Gymnasium | 1 | 600 | 600
Rehabilitation | 1 | 1200 | 1200
Support
Nurse Station | 1 | 250 | 250
Clean Utility | 1 | 100 | 100
Dirty Utility | 1 | 100 | 100
Staff Toilets | 2 | 40 | 80
Inpatient Holding | 1 | 150 | 150
Wheelchair Alcove | 1 | 200 | 200
Housekeeping Closet | 2 | 20 | 40
Sub-Total |  |  | 3620
Add : Circulation @ 30% |  |  | 1086
Total |  |  | 4706
Radiology / Imaging & Diagnostics
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Reception / Registration / Report Collection | 1 | 200 | 200
Central Waiting Space | 1 | 500 | 500
1000 ma X-Ray Room + Toilet + Change | 1 | 400 | 400
500 ma with Fluoroscopy Room + Change + Toilet | 1 | 400 | 400
Ultrasound Scan Rooms + Toilet | 2 | 150 | 300
Mammography | 1 | 120 | 120
CT Scan + Equipment | 1 | 400 | 400
MRI + Equipment | 1 | 500 | 500
Common Computer/Console Room | 1 | 200 | 200
Diagnostics
Cardio-Pulmonary Lab (Echo, Stress & PFT) | 1 | 350 | 350
Patient Changing Room and Toilet | 1 | 80 | 80
Office (Radiologist, Sonologist) | 1 | 120 | 120
Support
Reporting Office | 1 | 150 | 150
Common Dark Room | 1 | 80 | 80
Unexposed Film & Chemical Store | 1 | 100 | 100
Staff Toilet | 2 | 40 | 80
Housekeeping Closet | 1 | 20 | 20
Sub-Total |  |  | 4000
Add : Circulation @ 25% |  |  | 1000
Total |  |  | 5000
Dialysis Unit
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Reception and Waiting | 1 | 200 | 200
Dialysis Units | 12 | 120 | 1440
Dialyser Store | 1 | 120 | 120
Clean Utility | 1 | 80 | 80
Dirty Utility | 1 | 80 | 80
Ositive and Negative Wash | 1 | 100 | 100
RO Plant | 1 | 100 | 100
Sub-Total |  |  | 2120
Add : Circulation @ 30% |  |  | 636
Total |  |  | 2756
Radiation Therapy
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Reception/Waiting/Lounge | 1 | 500 | 500
Liner Accelerator Bunkers | 2 | 1200 | 2400
Simulator/CT Scan | 0 | 350 | 0
Control Room | 2 | 120 | 240
Gamma Knife | 1 | 450 | 450
Inpatient Waiting | 1 | 200 | 200
Dark Room | 1 | 80 | 80
Block Room | 1 | 100 | 100
Exam/ Consult Room | 2 | 120 | 240
Patient Change Areas | 4 | 30 | 120
Dosimetry | 1 | 150 | 150
Mold Room | 1 | 200 | 200
Brachytherapy | 1 | 400 | 400
Patient Change Areas | 2 | 30 | 60
Private Treatment Cubicles | 2 | 100 | 200
Procedure Room | 1 | 180 | 180
Support
Nurse's Workstation | 1 | 150 | 150
Patient Toilet | 2 | 40 | 80
Staff Toilet | 1 | 40 | 40
Office-Chief Technician | 1 | 100 | 100
Cleean Utility | 1 | 80 | 80
Dirty Utility | 1 | 80 | 80
Pantry | 1 | 80 | 80
Stores | 1 | 120 | 120
Equipment bay | 2 | 80 | 160
Wheelchair/stretcher Bay | 1 | 50 | 50
Housekeeping Closet | 1 | 20 | 20
Sub-Total |  |  | 6480
Add : Circulation @ 30% |  |  | 1944
Total |  |  | 8424
Nuclear Medicine
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Reception/Workstation | 1 | 80 | 80
Patient Changing Cubicle | 1 | 30 | 30
Patient Toilet | 1 | 40 | 40
Patient Toilet (Hot) | 1 | 40 | 40
Gowned Patient Waiting Area | 1 | 100 | 100
Inpatient Holding Area | 1 | 150 | 150
Thyroid Uptake/Scan Room | 1 | 120 | 120
Patient Injection/Recovery Cubicle | 1 | 80 | 80
Patient Injection Room | 1 | 100 | 100
Gamma Camera | 1 | 400 | 400
PET Room | 1 | 500 | 500
PET Control Room | 1 | 100 | 100
PET Computer Room | 1 | 80 | 80
Laser/Imager Processor Station | 1 | 60 | 60
Physician Viewing/Reading Room | 1 | 120 | 120
Tech Work Area | 1 | 120 | 120
Supervisor Office Cubicle | 1 | 80 | 80
Hot/Radiopharmaceutical Lab | 1 | 100 | 100
Radioactive decay Storage | 1 | 60 | 60
Clean Utility | 1 | 80 | 80
Dirty Utility | 1 | 80 | 80
Staff Toilet | 1 | 40 | 40
Linen Storage Alcove | 1 | 20 | 20
Emergency Equipment Alcove | 1 | 20 | 20
Wheelchair/Stretcher Alcove | 1 | 40 | 40
Portable Equipment Alcove | 1 | 20 | 20
Sub-Total |  |  | 2660
Add : Circulation @ 30% |  |  | 798
Total |  |  | 3458
Operation Theater Complex & Day Care Unit
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
General OT's | 4 | 600 | 2400
Major OT's | 6 | 600 | 3600
Robotic Surgery OT + Support Space | 1 | 1200 | 1200
Sub-Sterile Room(with Flash Sterilizer) | 6 | 80 | 480
Scrub Areas | 6 | 50 | 300
Endoscopy Room | 2 | 300 | 600
Day Care Beds + Toilets | 12 | 80 | 960
General Equipment Storage Room | 2 | 150 | 300
Pre-Op Holding and Preparation ( 4 Beds )/Post-Op | 16 | 80 | 1280
Clean Utility | 1 | 120 | 120
Dirty Utility | 1 | 120 | 120
Support
OT Nursing Station | 1 | 200 | 200
Matron's Room | 1 | 100 | 100
Housekeeping Closet | 1 | 20 | 20
Stretcher Alcove | 2 | 50 | 100
Doctor's Lockers & Toilet | 1 | 1000 | 1000
Nurse's Locker & Toilet | 1 | 500 | 500
Class IV Locker & Toilet | 1 | 500 | 500
Doctor's lounge | 1 | 300 | 300
Staff Lounge | 1 | 300 | 300
Consultation / Quiet Room | 3 | 120 | 360
Sub-Total |  |  | 14740
Add : Circulation @ 30% |  |  | 4422
Total |  |  | 19162
Interventional Cardiology (Cath. Lab)
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Reception / Registration / File Storage | 1 | 200 | 200
Cardiac Catheterisation Laboratory | 2 | 500 | 1000
Angio Day Care Beds-Recovery | 8 | 100 | 800
Scrub Area | 2 | 30 | 60
Control room | 1 | 300 | 300
Equipment Room | 1 | 120 | 120
Patient Preparation and Toilet | 1 | 150 | 150
Inpatient Holding | 1 | 200 | 200
Sub Total |  |  | 2830
Add : Circulation @ 30% |  |  | 849
Total |  |  | 3679
Mother & Child with IVF
Description | Quantity | Area /Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Delivery Room / Toilet / Scrub | 2 | 350 | 700
Stand-By Labor Room with Toilet | 4 | 250 | 1000
LDR's | 2 | 400 | 800
Scrub Area | 2 | 50 | 100
Stretcher / Wheelchair Alcove | 2 | 50 | 100
Central Waiting | 1 | 400 | 400
Reception / Control | 1 | 150 | 150
Support
Nurse Station | 1 | 150 | 150
Clean Utility | 1 | 80 | 80
Dirty Utilty | 1 | 80 | 80
Housekeeping Closet | 1 | 20 | 20
IVF Lab
Recception & Waiting | 1 | 150 | 150
Patient Change Room + Toilet | 1 | 80 | 80
Doctor's Change Room + Toilet | 1 | 120 | 120
Semen Collection Room + Toilet | 1 | 100 | 100
Exam & Consult Room | 1 | 120 | 120
IVF Lab | 1 | 200 | 200
IUI Lab | 1 | 120 | 120
OT | 1 | 250 | 250
Recovery Room (3 Beds) | 1 | 300 | 300
Doctors Conference | 1 | 150 | 150
Housekeeping Closet | 1 | 20 | 20
Sub-Total |  |  | 5190
Add : Circulation @ 30% |  |  | 1557
Total |  |  | 6747
Nursery and NICU
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Well-Baby Nursery | 4 | 40 | 160
Scrub / Gown Area | 1 | 50 | 50
Neonatal Intensive Care Unit (4 Clean-4 Infected) | 8 | 90 | 720
Support
Nurse Station with Medicine Preparation | 1 | 200 | 200
Clean Utility | 1 | 80 | 80
Dirty Utility | 1 | 80 | 80
Housekeeping Closet | 1 | 20 | 20
Breast Feeding Rooms | 2 | 60 | 120
Family Waiting with Toilet | 1 | 400 | 400
Sub-Total |  |  | 1830
Add : Circulation @ 30% |  |  | 549
Total |  |  | 2379
Intensive Care Unit
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
SICU | 24 | 180 | 4320
MICU | 32 | 180 | 5760
ICCU | 12 | 180 | 2160
CT ICU | 12 | 180 | 2160
Neuro ICU | 12 | 180 | 2160
PICU | 12 | 180 | 2160
Patient Toilets | 6 | 40 | 240
Support
Equipment Storage | 3 | 100 | 300
Nurse Station ( with monitoring ) | 6 | 150 | 900
Clean Utility | 3 | 80 | 240
Soiled Utility | 3 | 80 | 240
Housekeeping Closet | 3 | 20 | 60
Pantry | 3 | 100 | 300
Wheelchair / Stretcher Alcove | 6 | 50 | 300
Doctor's Sleep Room with Toilet | 3 | 150 | 450
Quiet Room | 3 | 120 | 360
Relatives Dormitory with Toilets | 2 | 2000 | 4000
Family Waiting with Toilet | 1 | 1000 | 1000
Sub-Total |  |  | 27110
Add : Circulation @ 30% |  |  | 8133
Total |  |  | 35243
In-Patient Wing
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Suites | 4 | 730 | 2920
Private Rooms | 48 | 365 | 17520
Semi-Private Rooms ( 2 Beds each ) | 48 | 365 | 17520
4-Bed Wards | 12 | 730 | 8760
Support
Nurse Stations | 6 | 200 | 1200
Clean Utility | 6 | 120 | 720
Soiled Utility | 6 | 120 | 720
Floor Pantry | 6 | 150 | 900
Wheelchair / Stretcher Alcove | 6 | 100 | 600
Housekeeping Closet | 6 | 20 | 120
Staff Toilet | 6 | 50 | 300
Family Waiting with Toilet | 8 | 450 | 3600
Sub-Total |  |  | 54880
Add : Circulation @ 30% |  |  | 16464
Total |  |  | 71344
Central Sterilization & Processing Department
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Soiled Work Room (Receiving, Sorting) | 1 | 300 | 300
Inspection, Wrap and Pack Area | 1 | 400 | 400
Sterilization Area | 1 | 200 | 200
Storage and Dispensing Area | 1 | 500 | 500
CSSD Managers Room | 1 | 100 | 100
Staff Change Room | 2 | 80 | 160
Staff Toilet | 2 | 30 | 60
Sub-Total |  |  | 1720
Add : Circulation @ 20% |  |  | 344
Total |  |  | 2064
Clinical Laboratory & Blood Bank
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Open Lab | 1 | 1000 | 1000
Microbiology | 1 | 250 | 250
Histopathology | 1 | 250 | 250
Pathologist's Office | 1 | 120 | 120
Blood Bank with Components | 1 | 2000 | 2000
Store | 1 | 200 | 200
Reporting Room | 1 | 200 | 200
Wash Area | 1 | 80 | 80
Staff Toilet | 2 | 30 | 60
Sub-Total |  |  | 4160
Add : Circulation @ 20% |  |  | 832
Total |  |  | 4992
Kitchen and Dining
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Kitchen including Kitchen Stores | 1 | 2000 | 2000
Dietitian's Office | 1 | 120 | 120
Serving and Handwash Area | 2 | 200 | 400
Doctors & Visitor Dining (50 seating) | 1 | 1000 | 1000
Dining Area ( 100 seating ) | 1 | 1500 | 1500
Housekeeping Closet | 2 | 20 | 40
Sub-Total |  |  | 5060
Add : Circulation @ 20% |  |  | 1012
Total |  |  | 6072
Administration
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Chief Executive Officer | 1 | 250 | 250
CEO's Private Secretary + Waiting | 1 | 150 | 150
Chief of Nursing | 1 | 150 | 150
Managers (Finance/Admin/Personnel/Marketing) | 4 | 120 | 480
Assistant Managers | 8 | 80 | 640
Secretaries / Other Staff | 25 | 50 | 1250
Telephone Operator | 6 | 50 | 300
EDP / Copier etc. | 1 | 300 | 300
Files / Storage | 1 | 400 | 400
Library cum Conference Room ( 20 seater ) | 1 | 500 | 500
Board Room | 1 | 600 | 600
Teaching/Seminar Hall | 1 | 1200 | 1200
Visitor Waiting | 1 | 300 | 300
Executive Toilets | 2 | 40 | 80
Staff Toilets | 2 | 40 | 80
Housekeeping Closet | 1 | 20 | 20
Sub-Total |  |  | 6700
Add : Circulation @ 20% |  |  | 1340
Total |  |  | 8040
Materials Management, Housekeeping, Laundry & Staff Lockers
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Loading / Unloading Dock | 1 | 200 | 200
Breakdown / Sorting Area | 1 | 250 | 250
Bulk Storage | 1 | 1000 | 1000
Dispatch / Receiving Office | 1 | 120 | 120
Hospital Supply Pharmacy | 1 | 750 | 750
Materials Manager's Office | 1 | 120 | 120
Executive Housekeeper's Office | 1 | 120 | 120
Clerical Staff | 5 | 50 | 250
Soiled Linen | 1 | 200 | 200
Laundry | 1 | 1750 | 1750
Mortuary (4 Cabinets) | 1 | 200 | 200
Housekeeping Closet | 4 | 20 | 80
Lockers
Nurses Lockers / Toilets | 1 | 750 | 750
Class IV Female Staff Lockers / Toilets | 1 | 500 | 500
Class IV Male Staff Lockers Toilets | 1 | 500 | 500
Sub-Total |  |  | 6790
Add : Circulation @ 25% |  |  | 1697.5
Total |  |  | 8487.5
Electrical, HVAC, Maintenance & Biomedical Engineering
(To be confirmed with Services Consultants)
Description | Quantity | Area / Room | Total Area
|  | (Sq. Ft.) | (Sq. Ft.)
Manager's Office | 1 | 120 | 120
Engineers / Clerical Staff | 6 | 50 | 300
General Maintenance Workshop | 1 | 750 | 750
Bio-Medical Engineering Workroom | 1 | 350 | 350
Boilers & Mechanical Equipment | 1 | 4000 | 4000
Medical Gas Manifold Room | 1 | 500 | 500
Electrical Panels & D.G. Sets | 1 | 2500 | 2500
Sub-Total |  |  | 8520
Add : Circulation @ 20% |  |  | 1704
Total |  |  | 10224